## BOQ
Bill of quantities · kitchen · Cabin East, Betalbatim
Shop 4, Tulip Residency, Gandaulim, Salcete, South Goa. Kitchen 4.9 × 2.4 m, one chef and one helper. Quantities and sizes come from the model and the two A3 sheets (kitchen.html); measure on site before ordering.
Fill the yellow cells (rate, make/model, remarks). Amounts and totals calculate. Rates ex-GST, itemised; freight, installation and the GST rate go in the lines at the bottom. Sizes are width × depth × height in mm, the space available.
Item | Item / type | Size W × D × H (mm) | Capacity, rating, specification | Unit | Qty | Rate (₹) | Amount (₹) | Make / model / remarks | Drawing
A | Stainless steel fabrication (SS 304 throughout) |  | Worktops 1.2 mm or thicker, bodies 1.0 mm, legs 38 mm tube, welded and polished joints, adjustable feet. Supplier confirms or corrects the gauges.
A.01 | Non-veg prep bench | 800 × 650 × 900 | Open undershelf for the board rack, 100 mm back upstand | nos | 1 |  |  |  | Sheet 1
A.02 | Dumpling and veg prep bench | 800 × 650 × 900 | Top over the under-counter freezer (B.07); two wall shelves over | nos | 1 |  |  |  | Sheet 1
A.03 | Pass counter | 650 × 650 × 900 | Heat-lamp bracket; hatch ledge 700 mm through the wall | nos | 1 |  |  |  | Sheet 1
A.04 | Dish sink, 2 bowls | 800 × 650 × 900 | Pre-rinse spray bracket, undershelf, legs | nos | 1 |  |  |  | Sheet 1
A.05 | Wall shelf over the dish line | 1,400 × 350 | One plain, one slatted for bamboo steamer baskets | nos | 2 |  |  |  | Sheet 1
A.06 | Veg and herb wash sink | 450 × 500 × 900 | Single bowl, legs, undershelf | nos | 1 |  |  |  | Sheet 1
A.07 | Sauce and oil wall shelf | 900 × 300 | Back-up stock, fixed at 1.45 m | nos | 1 |  |  |  | Sheet 1
A.08 | Wok seasoning rail | 440 × 220 | At 1.0 m; 8 lidded pots and a rack for 8 squeeze bottles | set | 1 |  |  |  | Sheet 1
A.09 | Wok tool rail | 470 long | At 1.4 m with 4 hooks | nos | 1 |  |  |  | Sheet 1
A.10 | Chilled mise-en-place rail | 760 × 260 × 220 | Counter-top unit for 5 pans | nos | 1 |  |  |  | Sheet 1
A.11 | Dip and garnish rail | 650 × 120 | 5 inserts, on the pass | nos | 1 |  |  |  | Sheet 1
A.12 | Ticket rail | 650 long | Above the pass hatch | nos | 1 |  |  |  | Sheet 1
A.13 | Magnetic knife strip | 400 long |  | nos | 2 |  |  |  | Sheet 1
A.14 | Cutting-board rack | 280 × 420 × 420 | Slots for 4 colour-coded boards, under the non-veg bench | nos | 1 |  |  |  | Sheet 1
A.15 | Floor channel drain | 3,150 × 80 | SS grating, falls to the grease trap | m | 3.15 |  |  |  | Sheet 1
A.16 | Canopy hood | 3,350 × 950 × 550 | Bottom edge at 2.05 m; baffle filters, grease cup, LED lights; overhang 0.20 m at the open end, 0.15 m over the wok range | nos | 1 |  |  |  | Sheet 2
A.17 | Exhaust ductwork | 400 × 400 section | SS at 2.35 to 2.75 m: hood collar, wall penetration, along the back wall, round the corner, to the ESP, fan and discharge; brackets, bends and access doors | m | 5 |  |  |  | Sheet 2 · measure on site
A.18 | Discharge elbow | 400 × 400 section | About 2.6 m high, pointing away from the building; bird mesh and rain cowl | nos | 1 |  |  |  | Sheet 2
A.19 | Storage deck racking | 450 × 2,050 · 1,900 × 450 · 800 × 450 | SS or galvanised, 3 tiers, one rack of each size | nos | 3 |  |  |  | Model
A.20 | Ceiling hatch frame with fold-down ladder | 600 × 800 opening | For light goods; heavy stock goes on the hoist (B.21) | nos | 1 |  |  |  | Sheet 1
Subtotal, section A
B | Cooking, cold and kitchen equipment (branded) |  | State make and model, kW or litres, and who services it in Goa. Sizes are the space available; do not quote a wider unit.
B.01 | Chinese wok range, 2 burners | 1,200 × 800 × 800 | LPG; state burner kW. 750 to 900 mm deep is acceptable (aisle is 0.95 m at the range) | nos | 1 |  |  |  | Sheet 1
B.02 | Dim sum steamer, 2 holes | 600 × 700 × 800 | LPG; with water top-up | nos | 1 |  |  |  | Sheet 1
B.03 | Twin-tank fryer | 600 × 700 × 900 | LPG; two tanks (veg and non-veg oil) | nos | 1 |  |  |  | Sheet 1
B.04 | Stock range, 2 burners | 600 × 700 × 850 | LPG; for 20 L stock pots | nos | 1 |  |  |  | Sheet 1
B.05 | Reach-in, 2 doors, dual temperature | 950 × 750 × 2,000 | About 800 L: fridge door at the front, freezer door at the back, doors open into the aisle; state litres of each side | nos | 1 |  |  |  | Sheet 1
B.06 | Under-counter fridge (pass) | 600 × 550 × 700 | Sauce bases and cut veg; state litres | nos | 1 |  |  |  | Sheet 1
B.07 | Under-counter freezer, 2 doors | fits under 800 × 650 | State litres (target about 650 L of freezer in all with the reach-in) | nos | 1 |  |  |  | Sheet 1
B.08 | Under-counter dishwasher | 600 × 650 × 900 | With drainboard and its own booster heater | nos | 1 |  |  |  | Sheet 1
B.09 | Rice cooker | Ø 260 | 5 L; one for jasmine, one for sticky rice | nos | 2 |  |  |  | Sheet 1
B.10 | Mixer-grinder |  | Commercial, for sauces and batter | nos | 1 |  |  |  | Sheet 1
B.11 | Kitchen blowtorch |  |  | nos | 1 |  |  |  | Sheet 1
B.12 | Storage water heater | Ø 330 × 500 | 35 L, 3 kW, 70 °C, high on the left wall over the dish line | nos | 1 |  |  |  | Sheet 2
B.13 | Water heater for a hand-wash basin |  | 6 L, under each basin | nos | 2 |  |  |  | Sheet 2
B.14 | Insect killer | 500 × 180 | Over the kitchen door | nos | 1 |  |  |  | Sheet 1
B.15 | Heat lamp over the pass |  | On its own switch | nos | 2 |  |  |  | Sheet 1
B.16 | ESP with carbon odour filter | 500 × 1,000 × 900 | Outside at 2.05 to 2.95 m | nos | 1 |  |  |  | Sheet 2
B.17 | Inline exhaust fan | Ø 440 | 4,000 to 5,000 m³/h; anti-vibration mounts, speed control | nos | 1 |  |  |  | Sheet 2
B.18 | Fresh-air intake fan | 500 × 480 | High on the back wall; interlocked with the exhaust | nos | 1 |  |  |  | Sheet 2
B.19 | Make-up air diffuser | 600 × 500 | Perforated, low velocity, in the kitchen ceiling | nos | 2 |  |  |  | Sheet 2
B.20 | Make-up air cooling coil with condenser | condenser 800 × 550 × 300 | 1.5 TR; condenser on the right side wall at about 3.0 m | set | 1 |  |  |  | Sheet 2
B.21 | Goods hoist |  | Electric, 200 kg, over the ceiling hatch, with limit switch | nos | 1 |  |  |  | Sheet 2
B.22 | Smallware |  | To the chef's list: carbon-steel woks, ladle, spatula, spider, wok brush, pans, food pans, knives, boards, stone mortar | lot | 1 |  |  |  | Chef
B.23 | Bamboo steamer stack | Ø 260 | 3 baskets and a lid, for the drying shelf (the steamer comes with its own baskets, B.02) | nos | 3 |  |  |  | Sheet 1
Subtotal, section B
C | Gas installation (licensed contractor, for the fire NOC) |  | Pressure test and a written certificate are part of the work.
C.01 | LPG cage | 350 × 1,700 × 1,600 | Locked and ventilated, on the right strip | nos | 1 |  |  |  | Sheet 2
C.02 | LPG cylinder with changeover manifold and regulator | 19 kg each | 4 on line and 1 spare, 95 kg in all | nos | 5 |  |  |  | Sheet 2
C.03 | Copper gas pipe | size by contractor | With clamps and sleeves: along the right outside wall at 1.3 m, in at the back corner, drop to the manifold at 0.4 m, along the back of the hot line | m | 9 |  |  |  | Sheet 2 · measure on site
C.04 | Gas solenoid valve |  | Weatherproof, outside on the entry; closes with the exhaust fan or the hood suppression | nos | 1 |  |  |  | Sheet 2
C.05 | Ball valve, one per appliance |  | On the manifold | nos | 6 |  |  |  | Sheet 2
C.06 | Flexible gas hose, certified |  | One per appliance | nos | 6 |  |  |  | Sheet 2
C.07 | LPG leak detector |  | With cut-off signal, low on the right wall | nos | 1 |  |  |  | Sheet 2
C.08 | Pressure test, commissioning and certificate |  |  | lot | 1
Subtotal, section C
D | Plumbing and drainage |  | Sizes and fittings by the plumber. All kitchen drains go to the grease trap, then the grey-water line (never the biodigester).
D.01 | Water sump, buried | 1,300 × 1,000 × 800 | 1,000 L, with lid and tanker inlet, under the garden | nos | 1 |  |  |  | Plan
D.02 | Pressure pump set with sediment filter and softener |  | 0.5 HP pump; fits in the water cabinet (D.03) | set | 1 |  |  |  | Sheet 2
D.03 | Water cabinet | 450 × 800 × 1,500 | Ventilated, on the right strip; fabrication included | nos | 1 |  |  |  | Sheet 2
D.04 | Cold and hot water pipe with fittings and isolation valves | CPVC or PPR | Cabinet to the kitchen along the strip, and the hot-water run to the sink and dishwasher | lot | 1 |  |  |  | Sheet 2 · about 20 m
D.05 | Hand-wash basin, wall-mounted | 330 × 400 and 250 × 250 | Hands-free tap and soap dispenser: one at the door, one at the prep corner | nos | 2 |  |  |  | Sheet 1
D.06 | Swan-neck wok tap |  | Wall-mounted, tall, at the wok range | nos | 1 |  |  |  | Sheet 2
D.07 | Mixer taps for the veg sink and the dish sink |  | Tall mixer tap for the veg sink; sink mixer with pre-rinse spray for the dish sink | set | 1 |  |  |  | Sheet 2
D.08 | Pot filler |  | Wall-mounted swing arm, cold, over the stock range | nos | 1 |  |  |  | Sheet 2
D.09 | Steamer water feed with isolation valve |  | At the back wall | nos | 1 |  |  |  | Sheet 2
D.10 | Grease trap | 450 × 450 | Outside back corner, with cover | nos | 1 |  |  |  | Sheet 2
D.11 | Drain pipe uPVC with fittings | 100 mm | Floor channel, sinks, hand-wash basins and dishwasher to the grease trap and grey-water line | m | 12 |  |  |  | Sheet 2 · measure on site
D.12 | Floor trap with grating |  | SS | nos | 2 |  |  |  | Sheet 2
Subtotal, section D
E | Electrical |  | Three-phase supply about 15 to 20 kW. The fridges, exhaust fan, ESP, lights and water pump are on the power backup. Point numbers are on sheet 2.
E.01 | Socket or switch points 1 to 14 |  | As marked on sheet 2 (fridge, freezer, rice cookers, mise-en-place rail, heat lamps, dishwasher, insect killer, hood and panel, pass fridge, grinder, heater isolator, hand-wash heaters, hoist), with their own MCBs where marked | nos | 14 |  |  |  | Sheet 2
E.02 | Kitchen sub-distribution board |  | With RCCB and MCBs, earthing and labelling | nos | 1 |  |  |  | Sheet 1
E.03 | Exhaust fan and ESP control panel |  | With hood-light switch and interlocks (fan, make-up air, gas solenoid, suppression) | nos | 1 |  |  |  | Sheet 2
E.04 | LED hood light | 300 × 200 | Vapour-proof | nos | 3 |  |  |  | Sheet 2
E.05 | LED ceiling panel | 600 × 600 |  | nos | 3 |  |  |  | Model
E.06 | Cable, conduit, trunking and fixings |  | For all kitchen points | lot | 1
E.07 | Emergency light and EXIT sign |  | At the rear door | set | 1 |  |  |  | Sheet 1
E.08 | Testing and commissioning of all circuits |  |  | lot | 1
Subtotal, section E
F | Civil and finishes |  | Quantities from the 4.9 × 2.4 m kitchen; add wastage as usual. Ceiling must be non-combustible (no PVC).
F.01 | Wall tiles, white glazed | 75 mm tile | To 2.1 m on the left wall and the partition, 0.85 to 2.1 m on the back and right walls; grout and corner trims | m² | 22.4 |  |  |  | Model
F.02 | Anti-slip epoxy floor, grey |  | With falls to the channel drain | m² | 11.8 |  |  |  | Model
F.03 | Cement-board ceiling at 2.70 m |  | Non-combustible, with frame and white paint | m² | 11.8 |  |  |  | Model
F.04 | Double-acting kitchen door | 800 × 2,050 | Stainless, spring pivots, vision panel, push plates and kick plate | nos | 1 |  |  |  | Sheet 1
F.05 | Rear exit door | 800 × 2,100 | Opening outward; closer, rubber sweep, PVC strip curtain and panic bar | set | 1 |  |  |  | Sheet 1
F.06 | Cutting and making good | 400 × 400 duct opening | Duct opening in the back wall, gas and water sleeves, fan and intake openings | lot | 1 |  |  |  | Sheet 2
F.07 | Storage deck over the kitchen | 4,900 × 2,400 | Plywood on steel joists, rated for storage only | m² | 11.8 |  |  |  | Model
Subtotal, section F
G | Fire and safety |  | Needed for the fire NOC.
G.01 | Wet-chemical hood suppression |  | Nozzles over each appliance, manual pull and automatic gas cut-off | set | 1 |  |  |  | Sheet 2
G.02 | Extinguisher, wet chemical (Class K) | 6 L | On the back wall at the end of the hot line | nos | 1 |  |  |  | Sheet 1
G.03 | Extinguisher, CO₂ | 4.5 kg | Beside the electrical board at the kitchen door | nos | 1 |  |  |  | Model
G.04 | Fire blanket in a wall box |  |  | nos | 1 |  |  |  | Sheet 1
G.05 | First-aid box |  | On the wall | nos | 1 |  |  |  | Model
G.06 | Heat detector |  | On the kitchen ceiling, wired to the alarm panel | nos | 1 |  |  |  | Sheet 2
Subtotal, section G
H | Outside, bins and housekeeping
H.01 | Bin store | 450 × 900 × 1,000 | Timber slats, on the right strip | nos | 1 |  |  |  | Plan
H.02 | Wheeled bin | 60 L | Wet, dry and glass | nos | 3 |  |  |  | Plan
H.03 | Foot-pedal bin | Ø 200 × 600 | Wet under the veg sink, dry by the rear door | nos | 2 |  |  |  | Sheet 1
H.04 | Steel bollard | Ø 130 × 900 | On the edge of the strip | nos | 6 |  |  |  | Plan
H.05 | Apron hook rail | 3 hooks | Above the prep-corner hand-wash | nos | 1 |  |  |  | Sheet 1
H.06 | Dirty-linen bag with lid; used-oil can with spill tray | oil can 20 L |  | set | 1 |  |  |  | Sheet 1
Subtotal, section H
Total of all sections (ex-GST)
Freight and unloading to Betalbatim
Installation and connections not included above
| GST rate (%) | [5 empty] | 18
GST
Grand total including GST

## Notes
How to use this BOQ
1. Send the same BOQ and the two A3 sheets to three suppliers per group: A (fabrication) to Gujarat, Mumbai and Goa fabricators; B to Goa dealers plus the brand or an online dealer; C to E to licensed contractors.
2. Suppliers enter the rate for every line (ex-GST), the make and model for section B, and remarks. A line left blank is not priced; do not compare totals until the line counts match.
3. Quantities marked "measure on site" (duct, gas pipe, drain pipe, water pipe) are estimates from the model; the contractor measures and re-prices by the metre.
4. Every quote must also state: steel grade and thickness, price ex-GST with the GST rate, delivery, installation, lead time, payment schedule, warranty and who services it in Goa, validity.
5. Concept drawings for briefing suppliers, not construction drawings.